PETROLEUM SAFETY TASK FORCE 2025

Petrol Stations Inspection

& Compliance Visitation to the Storage Terminals for Tongatapu

Department of Energy Report

PETROLEUM SAFETY TASK FORCE 2025 Petrol Stations Inspection & Compliance Visitation to the Storage Terminals for Tongatapu Department of Energy Report

Sione Hale ‘Akau; 4/1/26; [Course title].

## Background

Following the Petroleum Task Force Safety Inspection in 2021, the Tonga Competent Authority (TCA) requested the line Ministries cooperation to carry out the safety inspection of Petroleum Terminals as well as individual Service stations to make sure that they are comply with the safety requirements for the safety of the people and environment.

The Petroleum Task Force consists of representatives from:

- Consumer Protection & Fair-Trade Division (MTED)

- Tonga Fire and Emergency Department

- Department of Environment (MEIDECC)

- Department of Energy (MEIDECC)

- Building Control Division (MOI)

- Public Health (MOH)

The Department of Energy’s service stations inspection checklist is based on the following

- There should be emergency procedures for fire, spillage, accidents an equipment failure.

- All the employees must be trained and aware of these procedures so that they can be carried out in a timely manner. All attendants must be able to use safety equipment at the Gas Station.

- Spill Kits must be in the Gas Station as well as First Aid Safety Kits

- A list of emergency numbers that includes, fire Dept., ambulance and the police, should be prominently displayed.

- There must be a main emergency switch that cuts of power to all pumps units. This emergency stops should be in an accessible place and must not be blocked.

- Site Plan and Risk Assessment: A risk assessment ensures that the property owner is aware of all the potential dangers that are present on the site and all the steps are being taken to mitigate those risks.

## SERVICE STATIONS INSPECTION FOR TONGATAPU

The Petroleum Task Force was originally scheduled to commence on Monday, 6 October and run through to 10 October. However, due to adverse weather conditions, the program was postponed and instead took place from 7–10 October.

### The findings identified by the Department of Energy are presented in the table below.

| No. | Service Stations | Findings |
| --- | --- | --- |
|  | Cocker Enterprise Ma’ufanga (TOTAL) | - Staff are not aware of emergency response procedures for fire incidents, fuel spills, or equipment malfunction. - Only 1 employee is present and has no knowledge of safety guidelines. - No spill kit or first aid kit available on-site. - Emergency contact numbers are not displayed. - The pump main switch has been identified and is accessible. - No site plan or risk assessment is available. - Electrical wiring is untidy and poorly arranged. |
|  | Konifelenisi Ma’ufanga (TOTAL) | - No emergency procedures are in place for fire, spillage, or equipment failure. - Employees have not received any safety or emergency response training. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - The main switch for the pump is identified and accessible. - No site plan or risk assessment is available. |
|  | Luna’eva Pahu (PE) | - Emergency procedures for fire, spills, and equipment failure are communicated to employees by the supervisor. - Employees have received training from the Fire Department. - Total staff: 9 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - The pump main switch is identified and accessible. - No site plan or risk assessment is available. |
|  | Cocker Enterprise Hala Fatafehi (TOTAL) | - No emergency response procedures are available on-site. - Employees have not received training. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible to employees. - No site plan or risk assessment is available. |
|  | EM Jones Kolofo’ou (PE) | - No emergency procedures are available. - Employees have not received training. - Total staff: 2 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible to employees. - No site plan or risk assessment is available. |
|  | Tevita Tu’itupou Kolomotu’a (TOTAL) | - No emergency procedures - No training for employees - 2 employees - No Spill kits and No First Aid kit - No List of emergency numbers displayed - Main switch for the pumps identified and it is accessible for employees - No site plan and risk assessment |
|  | Lisiate Raass Sopu (PE) | - Employees are not familiar with emergency response procedures. - One employee has attended PE training. - Total staff: 2 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan or risk assessment is available. |
|  | Luna’eva Maui, Hala Hihifo (PE) | - Staff are briefed by the supervisor on emergency response procedures and general safety. - Employees have received training from the Fire Department. - Total staff: 10 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan or risk assessment is available. |
|  | MJ Hofoa Station Hofoa (TOTAL) | - No emergency response procedures are in place. - Employees have not received training. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Main switch is in a locked room and is not accessible to all employees. - No site plan or risk assessment is available. - Employees are Fijian, not speaks English or Tonga Fluently |
|  | Sia’atoutai Gas Station Sia’atoutai (TOTAL) | - No emergency procedures are available. - One employee has attended Fire Department training. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible to employees. - No site plan or risk assessment is available. |
|  | Vaitohi Nukunuku (PE) | - No emergency response procedures are in place. - No employee training has been conducted. - Total staff: 1 employee. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | Konifelenisi Trading Fanga ‘o Pilolevu (PE) | - No emergency procedures are available. - No training has been provided to employees. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible, however the wiring is unsafe. - No site plan is available. |
|  | EM Jones Koloua, Tofoa | - No emergency procedures are in place. - Employees have not received training. - Total staff: 3 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | EM Jones Pea | - No emergency procedures are available. - One employee has participated in PE training. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | Manu Family Tokomololo | - No emergency procedures are in place. - No employee training has been conducted. - Total staff: 3 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is located inside the shop and is only accessible to two employees. - No site plan is available. |
|  | Lopaukamea Veitonga (TOTAL) | - No emergency procedures are available. - No employee training has been conducted. - Total staff: 7 employees. - No spill kit or first aid kit available. - Emergency contact numbers are displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | Luna’eva – Veitongo Veitongo (PE) | - Employees are not aware of emergency response procedures. - Employees have received Fire Department training. - Total staff: 13 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified, but only the cashier and supervisor are allowed access. - No site plan is available. |
|  | Palu Trading Vaini | - No emergency procedures are in place. - No employee training has been conducted. - Total staff: 6 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | Palu Trading Malapo | - No emergency procedures - No emergency procedures are available. - No employee training has been conducted. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible, however there are two separate switch locations. - No site plan is available. |
|  | Palu Trade Fua’amotu | - No emergency procedures are in place. - No employee training has been conducted. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | FWC Tatakamotonga Tatakamotonga | - No emergency procedures are available. - No employee training has been conducted. - Total staff: 5 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan is available. |
|  | Sione Galliee Lapaha | - No emergency procedures are in place. - No employee training has been conducted. - Total staff: 3 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is located inside the shop and is accessible to both employees and customers. - No site plan is available. |
|  | Liu Gas Station Manuka | - Employees are briefed by the supervisor on emergency procedures and safety measures. - Employees have participated in Fire Department training. - Total staff: 4 employees. - No spill kit or first aid kit available. - Emergency contact numbers are not displayed. - Pump main switch is identified and accessible. - No site plan is available. |

## Recommendations for Service Stations

### Develop and Display Emergency Procedures

All stations should prepare and display clear emergency procedures for:

- Fire incidents

- Fuel spillage

- Equipment or pump failure

These procedures should be printed, laminated, and posted in visible areas such as:

- Inside the shop

- Near the pump area

- Staff office or cashier counter

### Conduct Mandatory Safety and Emergency Training

All stations must ensure that employees receive proper training on:

- Fire response and evacuation

- Spill containment and clean-up procedures

- Safe fuel handling

- Use of fire extinguishers

- Emergency shutdown procedures (main switch)

Training should be conducted regularly, preferably:

- Every 6 months (refresher training)

- For all new employees upon recruitment

Collaboration with the Fire Department and relevant authorities is strongly recommended.

### Provide Spill Kits and First Aid Kits

Every station must have:

- A complete spill kit (absorbent materials, gloves, disposal bags, etc.)

- A fully stocked first aid kit

These should be placed in accessible locations and checked monthly to ensure supplies are not expired or missing.

### Display Emergency Contact Numbers

Each station must display a list of emergency contact numbers, including:

- Fire Department

- Police

- Ambulance / Health Services

- Electricity / Power Authority

- Station Manager / Owner contact

This list should be displayed at minimum in:

- The shop counter area

- Pump area

### Ensure Accessibility of Pump Main Switch

The main pump shutdown switch should:

- Be clearly labelled

- Always be accessible to all employees

- Not be locked or restricted to only supervisors (unless alternative emergency shutdown access is provided)

Special attention should be given to stations where switches are locked in separate rooms or inside shops.

### Preparing a Site Plan and Risk Assessment

All stations should develop:

- A station layout plan showing pump locations, storage tanks, emergency exits, and fire equipment

- A risk assessment identifying hazards and mitigation measures

These documents should be updated annually and made available for inspections.

### Improve Electrical Safety and Wiring Standards

Stations with unsafe or messy wiring must:

- Engage certified electricians to inspect and repair wiring

- Ensure wiring is properly secured and protected from exposure

- Ensure all electrical installations meet safety standards

This is critical to reduce risk of fire and electrical accidents.

### Establish Routine Safety Inspections

Station operators should implement routine inspections to ensure compliance, including:

- Weekly safety checks (switch access, cleanliness, hazards)

- Monthly inspection of spill kit, first aid kit, extinguishers

- Annual safety audit with authorities

### Assigning a Safety Officer / Responsible Supervisor

Each station should assign a person responsible for:

- Safety compliance

- Staff training monitoring

- Updating emergency procedures

- Ensuring spill kits and first aid kits are maintained

This role can be assigned to the supervisor or station manager.

### Improve General Site Housekeeping

Stations should maintain clean and organized premises by:

- Removing unnecessary clutter near pump areas

- Keeping electrical and pump areas clear

- Ensuring proper waste disposal

Good housekeeping reduces fire risk and improves workplace safety.

## SAFETY COMPLIANCE VISITATION TO THE STORAGE TERMINALS FOR TONGATAPU

### TOTAL Energies Terminal

Total Energies operates as part of a Fiji consortium and is managed from Fiji. Although the company did not provide storage capacity data, it confirmed planned investment to upgrade storage by decommissioning four 7KL tanks and installing seven new 12KL underground tanks.

The Total Energies facility was observed to be well maintained, with strong safety practices in place. The site uses SCADA systems to prevent overfilling, emergency shut-off valves, and sensors to detect spills and vapors connected to alarms. The gantry includes earthing systems that prevent fueling if not properly connected, and safety harnesses are available for staff.

Maintenance practices appeared strong, with clearly numbered valves, updated painting, visible signage, and multiple spill response stations. The site also had fully equipped spill response trailers, including one specifically for ship bunkering leaks. The fire system includes three high-volume pumps drawing from a 10KL seawater tank, which also supports Pacific Energy in emergencies.

Overall, Total Energies was assessed as better managed and better equipped to reduce operational and safety risks compared to Pacific Energy. The report notes that Total Energies continues investing in safety and storage improvements, despite receiving a lower return on investment compared to Pacific Energy.

### Pacific Energy Terminal

Pacific Energy Tonga operates under an independent Pacific group registered in French Polynesia. In Tonga, the company manages three supply depots (including one at the airport), 19 service stations, and employs 22 staff. In 2024, Pacific Energy supplied around 41.6 million litres of fuel (ULP, Jet A1, kerosene, and small amounts of diesel), accounting for approximately 80% of Tonga’s fuel market.

Although Pacific Energy has safety and environmental policies displayed on-site, the inspection found several operational weaknesses. Signage was faded, poorly positioned, and difficult to read. Vehicle access into the facility was not properly monitored, and gates remained open during the inspection. PPE requirements were not fully met, with staff using non-certified helmets and not wearing gloves.

Firefighting systems were available (foam and extinguishers), but the foam supply was limited. The fire hydrant system relied on Total Energies staff to manually activate pumping, and the hydrant infrastructure was in poor condition with no maintenance records provided. Containment areas had standing rainwater, reducing spill capacity, and equipment showed signs of deterioration.

The gantry and associated equipment appeared poorly maintained. Earthing systems were not tested, and safety measures during tanker filling were inadequate (e.g., no safety harness used). General facility infrastructure such as handrails, stairs, and valves showed significant rust and deterioration.

Spill response capability was weak, with limited spill kits and an empty emergency spill trailer. Two sludge tanks were out of service and due for removal, with no clear replacement plan. Overall, the facility showed signs of inadequate maintenance and increased risk of failure, despite claims of regular training and procedures.