PETROLEUM SAFETY TASK FORCE

Petrol Stations Inspection

& Compliance Visitation to the Storage Terminals for Ha’apai

Department of Energy Report 2025

Team from the Energy Department Ha’apai

Mrs. Siniua Hoeft- OIC

Mr. Manase Tapu- Energy Officer

Inspection Checklist (Energy Department)

- Emergency procedure for fire, spoilage, accidents, and equipment failure

- Spills kits and first aid must be at the Gas Station

- List of emergency contact numbers that include, fire department, ambulance, and the police displayed

- The main emergency switch should be accessible

- Site plan and Risk Assessment

Service Station Inspection for Ha’apai

| No . | Service station | Finding |
| --- | --- | --- |
| 1 | Paumolevuka Location: Lotofoa Supplier: Total energy | - No first aid kit - No spill kit - No emergency number display - No site plan - No training for employee - Private station - One employ |
| 2 | Kalamafoni Location: lotofoa Supplier: Totally energy | - No first aid kit - No spill kit - No emergency number display - No training for employee - No site plan - One of the fire distinguish need to refill - 2 employ |
| 3 | Manatu’I au Location: lotofoa Supplier: pacific energy | - No training for employee - No spill kit - No first kit - No emergency number display - No site plan - Main switch is accessible and lock in a separate room beside the shop - This location is two separate business the service station is owned by one person - 3 employs |
| 4 | Talikavenga # 1 Location: Pangai Supplier: Pacific Energy | - No spill kit - First aid kit available inside office - 2 employs - No training for employee - Old pump with no emergency switch - Main switch is accessible - No emergency number displayed - 2 station in different location |
| 5 | Talikavenga # 2 Location: Pangai Supplier: Pacific energy | - No spill kit - No training for employee - No emergency number displayed - No first aid kit - Main switch is accessible - No emergency switch - 2 employs - No site plan |
| 6 | Vaitohi Location: Pangai Supplier: Total energy | - No spill kit - No first aid kit - No training for employee - 1 employs - No site plan - No emergency switch - Manual - No emergency number displayed |
| 7 | Latiume Location: Hihifo Supplier: Total energy | - No first aid kit - No spill kit - No training for employee - 1 employs - No emergency switch - Manual - No emergency number displayed - No site plan |

| 8 | Sisimaile Location: Hihifo Supplier: Pacific eneergy | - No spill kit - No training for employee - No first aid kit - 1 employs - No site plan - No emergency number displayed - Manual - One fire extinguishers need to replace |
| --- | --- | --- |
| 9 | Feleniu Location: ‘Uiha Supplier: Pacific energy | - No spill kit - No first aid kit - No emergency procedure - No training for employees - No emergency number displayed - No emergency switch - No site plan - Manual |

Issues that need to be addressed immediately

- Some service stations still operate the old petrol pumps; the newer upgrades have an emergency off switch. For safety reasons, all service stations should upgrade to the newer version.

- A lot of the fire extinguishers at the service stations either need to be refilled or replaced. This issue should be enforced to ensure that the service stations comply with basic safety standards.

- Needed to do training for the employee about the safety

Recommendations by the Team

The Department acknowledges the importance of this taskforce and is willing to continue participating in these inspection activity moving forward. It is obvious that the basic safety practices at these service stations are severely lacking. The department recommends that the reports from this taskforce should be circulated to the service stations so attempts could be made to improve safety and standards therefore in the future inspections we can be able to gauge any improvements made by the service stations.

Training of service station employees is a challenge as the people employed are usually on a short term basis. Rarely an employee at these service stations last more than two years let alone a full year. However, the service stations should provide basic things like displaying emergency contact numbers, having spill kits available and an evacuation site plan.

Finally, the Department proposes developing a Code of Practices for the following.

- Standards for designing and constructing services stations

- Petroleum storage and transport

- Products handling

- Storage and handling

- Protection from fire hazards

- Safety management documentation

- Weights and Measures standards for dispensing petroleum products

- Health and Safety for employees

- Training programs

- Ensuring customer safety

- Potential theft awareness

- Safe driving measures

- Assessment of harm

- Displaying the correct price for fuel

Safety Compliance Visit to the Storage Terminals for Tongatapu.

The task force conducted special training before continuing to inspect both Terminals. This included checking that each member had appropriate safety gear (shoes, shirt, trousers, helmet, glasses). Safety equipment is a must onsite, especially helmets that should be worn at all times except certain ‘green zone areas’ and these are marked. This introductory training is mandatory not only for employees at the site but for all visitors as well. No issues or concerns after the visit to both terminals.