Findings on the Petroleum Safety Task Force Program Tuesday 07th & Wednesday 08th September 2021 – Petrol Stations Tongatapu.

27 Petrol Stations in Tongatapu.

18 stations – Pacific Energy

9 Stations – Total (Fj) Ltd.

Checklists for individual ministry .

| MTED | - correct price at pumps - LPG agents or not? - How many pumps? |
| --- | --- |
| Fire & Emergency Services |  |
| Environment Dept |  |
| Public Health |  |
| Energy Dept – Some General Views | - There should be emergency procedures for fire, spillage, accidents an equipment failure. All the employees must be trained and aware of these procedures so that they can be carried out in a timely manner. All attendants must be able to use safety equipment at the Gas Station. - Spill Kits must be in the Gas Station as well as First Aid Safety Kits - A list of emergency numbers that includes, fire Dept., ambulance and the police, should be prominently displayed. - There must be a main emergency switch that cuts of power to all pumps units. This emergency stops should be in an accessible place and must not be blocked. - Site Plan and Risk Assessment: A risk assessment ensures that the property owner is aware of all the potential dangers that are present on the site and all the steps are being taken to mitigate those risks. |
| Building Control - MOI |  |

Findings

| Petrol Station | Ministry | Findings |
| --- | --- | --- |
| - Konifelenisi Trading – Fanga ‘o Pilolevu Supplier : Pacific Energy | MTED | - 4ULP Pumps - 2 ADO (I working & 1 broken) - Retail price on pump is correct. |
|  | Fire & Emergency Dept | - 2 safety signs - 2 Fire extinguishers |
|  | Environment Dept |  |
|  | Public Health |  |
|  | Energy Dept | - concern if the staffs at the station especially pump attendants have been well trained on safety awarenesses. |
|  | Building Control Div, MOI |  |
| - Asco Motors – Mailetaha Supplier : PE | MTED | - 2 ULP, 2 ADO Pumps - Retail price is correct - Also an LPG agent |
|  | Fire & Emergency Dept | - 2 safety signs - 2 Fire Extinguishers (1 full, 1 empty) - LPG cylinders cage - Separate full fire extinguisher for LPG. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | Building Control - MOI |  |
| - EM Jones – Kolofo’ou Supplier : Pacific Energy | MTED | - 2ULP , 2 ADO pumps - retail price is correct - LPG agent |
|  | Fire Department | - No Safety Signs at station for pumps - LPG refill too close to petrol pumps. - 3 Fire extinguishers (2 full & 1 needed recharge) - separate full fire extinguisher for LPG storage. - ULP pump needed to be replaced (tied with a rope) |
|  | Environment | -Complaint from the restaurant next door of the odours that the cylinders release from the re-fill has been referred to this department. |
|  | Public Health | - requests for the approval of the gas re-fill station to be in town and beside the petroleum pumps. |
|  | Energy Dept |  |
|  | MOI | - Building/Premise too close to the pumps. |
| - Cocker Enterprise – Hala Fatafehi Supplier : Total | MTED | - 8 ULP, 8 ADO pumps - Correct retail price on pumps |
|  | Fire Department | - Fire extinguishers (3 inside premise, 4 at pumps, all full, Foam ) - Water Supply - Safety signs |
|  | Environment |  |
|  | Public Health | - tidy area of business |
|  | Energy Dept |  |
|  | MOI |  |
| - Luna’eva – Pahu Supplier : PE | MTED | - 4 ULPs - 4ADOs (2 Broken) - Correct Retail Price |
|  | Fire & Emergency Dept | - 2 Fire extinguishers - 2 safety signs - no water supply |
|  | Environment |  |
|  | Public Health | - Health Certificate? |
|  | Energy Dept |  |
|  | MOI |  |
| - Cocker Enterprise – Ma’ufanga Supplier : Total (Fj) Ltd | MTED | - 4ULPs - 4ADOs - Correct retail price displayed |
|  | Fire Dept | - 4 safety signs - 4 fire extinguishers (2 at pumps, 2 inside premise) - Smoke alarm - Water Supply |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Walan Gas Station – Fangaloto Supplier : Total (Fj) Ltd | MTED | - 2 ULPs - 2ADOs (both broken) - Correct Price Display - LPG Agent - extra storage for ADO on ground instead of underground tank. 2500L |
|  | Fire Dept | - LPG cage complied - Water Supply - 4 Fire Extinguishers (2 Foams – full, 2 whites – empty) |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Discovery – Ma’ufanga Supplier : PE | MTED | - 2ADOs - 2ULPs - ADO Pumps displayed 2 different prices and have been reported to office while rejecting the pump. |
|  | Fire Dept | - displayed 2 safety signs - 2 fire extinguishers (both empty) - No water supply |
|  | Environment | - Leakage of ADO pumps |
|  | Public Health | - Baby staying inside premise |
|  | Energy Dept |  |
|  | MOI |  |
| - Lisiate Raass – Sopu Supplier : PE | MTED | - 2 ULP - 2 ADO (1 broken) - Correct retail price displayed |
|  | Fire Dept | - 2 empty fire extinguishers - no safety signs - no smoke alarm |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Telekava Station Supplier : Total (Fj) Ltd | MTED | - 2 ADOs - 2 ULPs - Correct retail price displayed |
|  | Fire Dept | - 2 (full) Fire extinguishers at pump, none in office - no smoke alarm |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Lunaeva Station – Maui Supplier : PE | MTED | - 2 ULPs - 2 ADOs - correct retail price displayed |
|  | Fire Department | - 2 Fire extinguisher outside both empty, 4 inside premise - 2 fire alarms - Water Supply |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - MJ Gas Station – Hofoa Supplier : Total (Fj) Ltd | MTED | - 2ULPs - 2ADOs - Correct retail price displayed on pump |
|  | Fire Dept | - 1 safety sign - 2 fire extinguishers at pump, 1 in premise. - 2 fire alarms - 5 water supplies (3 x 27,000L, 2 x 5000L) |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Sia’atoutai Gas Station Supplier : Total | MTED | - 2ULPs - 2ADOs - correct displayed retail prices |
|  | Fire Dept | - 3 safety signs - 2 fire extinguishers at pumps (both empty) - no smoking alarm |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Vaitohi – Nukunuku Supplier : PE | MTED | - 2 ULPs - 2 ADOs (1 working, 1 broken) - Correct retail price display |
|  | Fire Dept | - 4 fire extinguishers (2 outside, 2 inside) - 1 fire alarm - no water supply |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Lotoma’a Gas Station Supplier: PE | MTED | - 1ULP - 1 ADO - correct price displayed |
|  | Fire Dept | - 3 fire extinguishers (1 outside –empty, 2 inside premise) - 2 fire alarm - 2 safety signs - water supply. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - 150 Gas Station – Houma Supplier : PE | MTED | - 1 ADO - 1ULP - Correct price displayed - LPG Agent |
|  | Fire Dept | - underground tank too close to pump - LPG storage cage does not comply with 2metres away from entrance to premise - Building too close to pump and tank - 2 fire extinguishers (1 foam, 1 powder) - a separate full fire extinguisher placed for LPG cage. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI | - Posts at station too rusty and recommended for replacement - Recommend for a security camera for the premise |
| - Manu Family – Tokomololo Supplier : PE | MTED | - 1 ADO - 1 ULP - noted 2 seniti/litre discount - LPG agent |
|  | Fire Dept | - safety sign to be displayed outside at pump not inside the store. - Not complied with 25fts from tank to stations’s boundaries. - 2 full fire extinguishers - water supply provided |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI | - pipe for water supply – rusty |
| 18. Lopaukamea - Total | MTED | - 8 ULPs - 8 ADOs - LPG Agent - 2 seniti/litre discount |
|  | Fire Dept | - 2 Fire extinguisher (1 full, 1 empty) - security camera installed - safety signs installed - Water supply - Smoke alarm (1 working, 1 broken) - 2 fire extinguishers in premise (both empty) - no exit signs in premise |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - Luna’eva – Veitongo Supplier : Pacific Energy | MTED | - 4 ADOs - 4 ULPs - correct price displayed - LPG agent |
|  | Fire Dept | - 5 full fire extinguishers (3 outside, 1 LPG cage, 1 at premise) - safety signs - water supply. |
|  | Environment | - 1 ADO pump was leaking but according to Lunaeva staff, it was from when it was fixed my PE staff. |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| 20 . Palu Trading – Vaini Supplier : PE | MTED | - 4 ULPs - 2 ADOs - Business License due to renew - LPG Agent - Correct price displayed |
|  | Fire Dept | - 2 fire extinguishers (1 working, 1 broken) - extinguisher at LPG storage cage is broken - smoke alarm to be fixed - Any concern with the tyre shop next to the petrol station? |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI | -security camera not working |
| - Palu Trade – Malapo Supplier : PE | MTED | - 3 ADOs - 4 ULPs - LPG agent - Correct price displayed but digits at pumps are fading |
|  | Fire Dept | - safety signs to remove from old station to the new ones. And 2 extra signs for both stations. - No fire extinguisher inside premise - 1 Empty fire extinguishers, 1 full powder extinguisher. - No fire extinguisher at LPG storage cage. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept | - concern on the wiring of electricity at the premise |
|  | MOI |  |
| - Palu Trade – Fua’amotu Supplier : Total (Fj) | MTED | - 2 ULPs - 2 ADOs - LPG Agent - Correct Price Displayed |
|  | Fire Dept | - smoke alarm installed - Fire extinguishers (2 empty) – - Need extra fire extinguishers 2 in premise and 2 outside - Safety signs installed. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI | - no security camera |
| - FWC – Tatakamotonga Supplier : PE | MTED | - 2 ADOs - 2 ULPs - correct price displayed - LPG agent |
|  | Fire Dept | - 3 empty fire extinguishers - water supply |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept | - concern on the wires connect to light. |
|  | MOI | - tanks too close to pumps - tanks too close to premise as vehicles are parked on top of the tanks. - Petrol station needs a renovation asap |
| - Sione Galilee – Lapaha Supplier : PE | MTED | - 1 ULP - 1 ADO - LPG Agent - Correct retail price displayed |
|  | Fire Dept | - 2 safety signs - 2 full fire extinguishers (powder) - No separate fire extinguisher for LPG storage cage |
|  | Environment |  |
|  | Public Health | - pets (kitten) at premise (shop) |
|  | Energy Dept |  |
|  | MOI |  |
| - Liu Gas Station – Manuka Supplier : PE | MTED | - 1 ADO - 2 ULP - Correct retail price display - LPG agent |
|  | Fire Dept | - active smoke alarm - safety signs - separate Fire extinguisher for LPG storage cage - 2 Fire extinguishers at pumps (1 full, 1 empty) |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI | - no security camera |
| - E.M Jones Pea Supplier : Total | MTED | - 2 broken pumps - 4 ADOs - 2 ULPs - correct price displayed - LPG agent |
|  | Fire Dept | - 5 full fire extinguishers (4 outside, 1 in premise) - Exit sign at premise needed. - Needed 3 extra safety signs. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |
| - EM Jones – Koloua Supplier : PE | MTED | - 3 ULPs - 1 ADO - Broken pumps rejected at last test – 1 ADO, 1 ULP - Correct Retail price display - LPG Agent |
|  | Fire Dept | - separate Fire extinguisher for LPG cage - water supply - 4 full powder fire extinguishers - one safety sign but need an extra one. - Security camera installed. |
|  | Environment |  |
|  | Public Health |  |
|  | Energy Dept |  |
|  | MOI |  |